## Chapter Five:  PV Standards

Chapter 5    PV Standards

5.1. Existing Standards and Specifications

5.1.1 What is a Standard?

A standard is a norm that all interested parties have agreed upon, such as the width of a railway track, the spelling of a word, the size of a golf ball, the way a CD-ROM disc goes round, or the way a solar PV installation should perform.

There should be a standard for your PV system. Moreover, there should be standards for the components and materials used in the PV system, from the PV module itself, the charge-controller and the battery, right down to the wiring, junction boxes, and wall fixing screws. There should be standards; too, for all the loads you are likely to power with the system, beginning with the lights and water pumps.

Technical standard is a document, which describes a material (for example glass), component (for example charge controller) or system (for example solar home system). It, consists of the following:

- Test items (e.g. appearance, labels, and each of the important functions of the product. In the case of a charge controller, these might include set points, high voltage disconnect, temperature compensation, and the like)

- Technical requirements (for each test item)

- Test methods (for each test item)

- Sampling procedures.

- Quality assurance (for each test item, e.g. procedures for test failures and repeat testing)

5.1.2 Why are Standards Needed?

A need can arise to standardize a material, a product or a system from the manufacturers’ desire to have interchangeable products, from the public, or from the government.  Standards are needed to define the product technically, and define the various characteristics (length, width, weight and the various measures of its performance). Standards also define how these characteristics should be measured.

Case Study # 5

#### PV STANDARDS

Early in the history of the terrestrial utilization of PV, it was realized that product reliability would be an extremely important matter for the acceptance of PV as a viable energy source for the future. The very first step in defining a benchmark for PV product reliability was taken by the Jet Propulsion Laboratory of the California Institute of Technology (JPL).

At that time, JPL was the U.S. leader in promoting PV development.  In order to further production of PV modules, JPL initiated a program in 1975 to buy a large quantity or “block” of PV modules from manufacturers. “Large quantity” in those days meant 2 – 10 kWp.

In the tender to buy the PV modules, JPL established quality control methods and also acceptance test criteria for the purchased modules. This was the first time terrestrial PV modules had been subjected to any kind of quality control and acceptance test procedures.  Until JPL established its criteria, manufacturers tested their modules to internal procedures. Those manufacturers who wanted to sell to JPL had to accept JPL’s test requirements and allow a JPL inspector to observe the performance of their modules during the tests.

To the great surprise of practically all the manufacturers under contract to produce modules under this JPL program, their modules failed.  Some of the companies succeeded in identifying and solving the problem and salvaging their contracts, as for example:

- In one case, a module failed during humidity testing. The company found out that the cause was that the plastic coating to protect the cells repelled water, but not humidity.  Therefore, the solar metallization was corroding. The company had to develop a cell metallization process, which would not corrode in humidity. After the process was changed, the module was successfully tested and accepted by JPL.

- In another case, a module failed during temperature cycling. The company found that the temperature coefficient of the used materials was too great. As a result, the entire design of the module had to be changed before it could pass the test.

After this first “Block I”, JPL repeated the purchasing process four more times. In those Blocks (II – V), requirements for acceptance testing became even more stringent, based on the experiences of the previous Blocks. The JPL testing specifications became the  “Standard” that other buyers of PV modules started to use. Ultimately, a modified version of the Block V specification became the IEC standard for crystalline PV modules.

JPL established quality control methods and, in successive purchases, enforced higher and higher quality specifications. As a result, PV modules now come with a 20 – 25 year warranty. If JPL had not established these specifications, there would be no PV industry today.  What can be learned from this story?

- Any standard (test specifications) is better than having none. The standard is a benchmark against which every manufacturer can measure its product quality.

- Standards should be updated based on what is learned through their application.

- Utilizing standards will result in superior products.

5.2 How are Standards (Specifications) Established?

5.2.1 National or Regional Standards

National or regional standards are established within a country or region. Many countries have a national standards organization, which is usually a government agency. In Europe, standardization occurs at the national level, although in the European Union, the standardization body, which has the authority for PV, is called CENELEC (European Committee for Electrotechnical Standardization).  In the United States, the situation is more complex. There is no one government agency responsible for standardization. Many public and private organizations develop standards.  In the field of PV, the safety standards are established by UL (Underwriters Laboratories).   Other U.S. standards organizations relevant to PV are the IEEE (Institute of Electrical and Electronics Engineers) or ASTM (American Society for Testing Material).  Both are private, nonprofit organizations.

Despite such national and regional differences, in general, the process used to establish a standard is similar:

- Standards are developed based on the knowledge and experience of many experts. Typically, products or materials are tested in the laboratory and also under field conditions. The experts, who may be working for the government, for a manufacturer, or for a customer, form a committee and establish an initial draft.

- After an initial draft of the standard is written, the passing of a standard requires a consensus of the experts.

National and regional standards have limitations in a global economy.  A manufacturer producing a PV product in a particular country should test the product according to the pertinent national standard. If the product is sold in another country or region, however, the PV product has to be re-tested according to the standard of that country or region. This may require the modification of the product or, at a minimum, the expense of re-testing.

5.2.2 Global/International Standards for PV (IEC Standards)

The International Electrotechnical Commission (IEC) issues the globally accepted standards for PV. The IEC's principal activity is developing and publishing international standards and technical reports.  These international standards serve as references when drafting international tenders and contracts.

The IEC is a worldwide federation of national standards bodies (IEC member bodies). The work of preparing international standards is normally carried out through IEC technical committees. Each member body interested in a subject for which a technical committee has been established has the right to be represented on that committee. International organizations, and governmental and non-governmental bodies also take part in the work.

The IEC has recognized the need to develop international standards based on market demand. The standards work of the IEC is carried out by technical committees, subcommittees, and working groups. IEC standards prepared by the technical committees are then submitted to the full member national committees (IEC members) for a vote with a view to their approval as international standards. Publication as an international IEC standard requires the approval by at least two thirds of the member bodies. Because of this approval procedure, the completion time for IEC standards takes at least two to four years.

The IEC has already approved module standards , but is still working on the standards required for all other system components -- controller, battery, inverter, etc., -- as well as the standards for the reliability, sizing and performance of the total integrated solar home system.

Box 5.1 Advantages of Having an International (Global) Standard

Bad example: TV is a prime example of the problems that can arise, if national or regional standards are used for a global product. Several TV standards were established and adopted by different countries.  European countries, for example, use three or four different TV standards. As a result, anyone who wants to see TV programs from another country, must purchase a more expensive TV set, that is equipped with circuitry able to receive and process the signals utilizing different standards. To make things more complicated, the same problem exists with VCRs. If one wants to tape a program and take it to another country, a VCR in that country may not be able to play it, without a special VCR and also a special TV that are able to handle multiple systems.

Good example: Fax technology is a good example of the advantages of global standards. Fax machines were initially manufactured in Japan. Their use spread too quickly for development of either national or regional standards.  Thus fax machines can communicate with each other all over the world. This has helped the global market for fax machines to grow very quickly.

Good example:  The Compact Disk (CD) was the joint development of a Netherlands and a Japanese company.  Only one standard exists, even though one might assume that there would be at least two, corresponding to the nationalities of the two companies in the venture.

The fax and CD examples show the distinct advantage of having global standards, instead of national standards. This is especially important for PV because PV is already a global business. Components and systems are manufactured in numerous countries.  Therefore, the best scenario is to unify all standards activities into a global/international standard.

5.2.3 The Two Categories of IEC Standards for PV

##### A) Standards Developed Specifically for PV Applications

IEC standards originate from a request to write a standard for a certain product or system. The request becomes a “new work item” assigned to one of IEC’s technical committees (TC).  The IEC TC 82 handles PV. Within IEC TC 82, PV becomes a work item for one of the working groups (WG).

Technical Committee No. 82: Solar Photovoltaic Energy Systems has, at the moment, seven working groups:

WG 1: Glossary

WG 2: Modules, non-concentrating

WG 3: Systems

WG 5: Quality and certification

WG 6: Balance-of-system components

WG 7: Concentrator modules

JCGTC 82 / TC88/TC21/SC21A:  Decentralized Rural Electrification (DRE)

The members of the IEC working groups are experts acting in an individual capacity, from industry as well as from other technical or governmental organizations.

B)  Standards Developed for other applications could be used for PV

IEC standards established for other applications (for example, low voltage switches, low voltage connectors, wiring, and the like) could be utilized for PV applications. PV GAP will identify and review these standards to determine their applicability for PV. If the review shows that these standards are appropriate, PV GAP will list them as an IEC standard to be utilized for PV components and/or systems.

PV GAP has compiled a list of both the IEC standards for PV, and the IEC standards developed for other applications, which should also be utilized for PV. The list of most of these standards available as of January 2002 are attached as Appendices 3 and 4 respectively.  A list of IECQ publications can be found in Appendix 4.

A list of the open Work Items and their project leaders is also included in Appendix 3

5.2.4 PV GAP Recommended Specifications (PVRS)

Given the urgent need for PV standards, an interim solution was sought to provide internationally accepted PV “guidelines” in a shorter time period than the 2-4 years it takes to develop and establish an IEC standard.  The creation of PV GAP facilitated the development of a complementary system to achieve global consensus on new specifications for PV in no more than six months. These interim specifications are called “PV GAP Recommended Specifications” (PVRS).

The ultimate goal is still to test PV components and/or systems to international (IEC) standards. However, where no IEC standard exists, PV GAP will recommend that certain specifications be developed, based on the consensus of experts.   In such instances, PV GAP Recommended Specifications (PVRS) are the fastest way to achieve an interim global “benchmark” for a PV product. (See Appendix 5 for a list of PV GAP Recommended Specifications.)

PV GAP has established a Technical Specifications Committee to assure that its PVRSs are based on a wide consensus within the industry. This Committee has a broad and global representation and is open to anyone with proper qualifications.

The PV GAP Technical Specifications Committee as shown in Figure 5.1, may utilize one of the following as the basis of a PVRS:

- A national or regional standard; or,

- If the above are not available, one or more Committee members may submit a draft

National or Regional Standards

Several national or regional PV Standards developed over the years, have not been incorporated into the IEC system or differ slightly from existing IEC standards. These standards can be very valuable, given the general lack of PV standards. The global industry problem created by multiple national or regional standards has been described above. The advantage of reviewing these national or regional PV Standards by PV GAP and establishing a PVRS with those found acceptable is that this offers a global Specification that eliminates the need for country by country re-testing.

New Work Item Initiated by PV GAP

Members of PV GAP may also propose PV standards.  For example, the so-called “Product Quality Assessment Specification” (PQAS) for PV did not exist until recently. (Product Quality Assessment Specifications will be discussed section 5.4 below.) PV GAP initiated these specifications.  After the draft of the specifications was drawn up, the procedure for issuing the specifications followed the steps described previously.  Following the approval of the PV GAP Board, the resulting PVRS was submitted to IEC TC 82 as a new work item proposal.

Description of the process to establish a PVRS

A draft version of the specification is formulated and circulated among the members of the PV GAP Technical Specifications Committee. It is important to note, that the membership of the PV GAP Technical Specification Committee is open to any qualified person in any country. This provides a global consensus for the establishment of a PVRS. Suggested technical modifications are submitted to the Chairman of the Committee, who reconciles them into a second draft, which is circulated again. The final vote is then either held by correspondence (e-mail) or at a meeting of the Technical Specifications Committee.

The Technical Specifications Committee then sends the PVRS to the PV GAP Board. The PV GAP Board decides whether to accept the PVRS or to ask the Technical Specifications Committee to consider changes. After the PV GAP Board accepts a PVRS, it will be published as the interim Recommended Specification to be used until a corresponding IEC standard is completed. If the basis of the original draft PVRS was other than an IEC new work item, then the PVRS will be immediately submitted as a new work item proposal (NP)  to the appropriate IEC Technical Committee.  When the resulting IEC standard becomes available, the PVRS will be withdrawn and no longer be used.

At present (as of January 2002), the PV module standards used by PV GAP are the IEC approved module standards. PV GAP has issued Recommended Specifications for other components (charge controllers and  inverters),  and for total systems.

Case Study # 6

# THE DEVELOPMENT OF A CHARGE CONTROLLER FOR NAVIGATIONAL AIDS

One of the best applications for photovoltaic energy has been in the field of marine navigational aids.  However, substantial design efforts were required to overcome the harsh environmental factors associated with this application.

Most navigational aids are deployed in the middle of a body of water such as a sea or a river.  Depending on their location, they may be subject to extremely hot temperatures (in the Middle East, for example) or extremely cold temperatures (in Canada).  Their support structures are neither firm nor easily oriented towards the sun.  Moreover, birds frequently perch or build nests on the modules, fouling all exposed areas.

Various navigation authorities have issued product specifications, because standard products generally cannot meet reliability expectations in marine settings.

(Continued on next page)

The most significant difficulties associated with this application have occurred around system design, battery life and charge control needs. Two distinct approaches have been utilized: 1) the design of low-voltage modules with a significantly oversized battery and no controller, and 2) the use of a standard voltage module with a controller and a smaller battery that satisfies the application requirement.

This latter was utilized for the Suez Canal Authority after an early failure had been experienced. The type of buoy that controls vessels passing through the Suez Canal is an elastic buoy anchored to the bottom of the Canal. Its ability to rotate is limited; therefore, module energy production varies more widely than for a fixed installation.   Furthermore, the ratio of insolation from summer to winter is four times greater if the module is installed at the winter angle. The original installation was made at an intermediate angle.  The combination of the intermediate angle and the small rotational variance in some cases produced too much energy and boiled away the battery electrolyte.  In other cases, not enough energy was produced and the batteries discharged rapidly.

After a thorough analysis of the insolation was performed, new modules with adequate capacity were delivered and installed at a favorable angle for the lowest insolation level. This installation, combined with the use of a charge controller to avoid any overcharging, provided the solution for this vital waterway.

The Canadian Coast Guard utilized this important design decision, with a further requirement for environmental testing and a fail-safe system that ensures operation, even if the regulator circuitry fails.  In this way, the very real threat to life associated with a navigational light failure was completely avoided. The detrimental impact on the controller of the severe weather conditions in Canadian waters was resolved through the use of an anodized aluminum box with watertight glands for the access of cables.

A temperature compensating thermistor monitors the battery temperature and allows the voltage output of the controller to increase as the temperature goes down. This feature was needed for locations where very cold temperatures require higher voltages to fully charge the battery.  Low-voltage modules would not be able to charge a battery at temperatures below freezing levels.

The records of reliability for these controllers have been excellent, with a return rate of less than 0.01%.  The manufacturing success is the result of a detailed design effort, environmental tests under extreme conditions, and a thorough Quality Plan during the fabrication of the units.  This plan included incoming component inspection, PC board testing, sub-assemblies, and final testing and calibration of every completed unit.  The customer also performed an on-site sample inspection for every lot delivered.

PV GAP Recommended Specifications

(If No IEC Standard Exists)

###### Figure 5.1

###### National

or

Regional

Standard

Work Item Initiated by

PV GAP

PV GAP

PV GAP

Technical

Specifications Committee

PV GAP

Executive Board

PV GAP

Recommended Specifications (PVRS)

Submitted to IEC

via IEC National Committee as a

New Work

Item Proposal

(NP)

IEC Standard

Issued;

###### PVRS

is Withdrawn

5.3 When There Are No Published Standards

A PV manufacturer may seek product quality approval from PV GAP, even when there is no published IEC standard or PVRS for the component or material.  The procedure is as follows:

- The manufacturer must have a data-sheet that sufficiently describes the PV component or the material used in the production of a PV component (for example, interconnecting wires). The description has to include not only the physical dimensions, but also all the characteristics of the component (for example, temperature coefficient, normal temperature range, electrical parameters, and the like)

- The manufacturer has to expand the data-sheet into a component specification that fully describes:

- Any necessary terminology (for example, temperature coefficient, etc.)

- The test method (for example for solderability), including test conditions (for example, time, temperature, humidity, etc.) either referring to an IEC standard test or in absence of an IEC test to another test, which must be fully described.

- The developed material should be submitted to PV GAP for approval.

- The PV GAP approval process is identical with the approval process described in the development of the PVRS.

- The PVRS will be issued.

- A PQAS must also be prepared. PV GAP’s central office could help the manufacturer with the first draft.

- Testing has to be performed in an approved testing laboratory (either on the manufacturer’s premises, or at an independent testing laboratory) which has IECQ accreditation in accordance with ISO/IEC 17025).

When No Published Standard is Available

Figure 5.2

MANUFACTURER’S DATA SHEET

#### PV GAP

#### Standards Committee

Executive Board

Describing:

- Product

- Terminology

- Test methods and test conditions

PV GAP

Recommended Specification

(PVRS)

Submitted to IEC

via IEC National Committee as a

#### New Work

#### Item Proposal

(NP)

Product Quality Assessment Specification

(PQAS)

IEC Standard

Issued;

PVRS

is withdrawn

5.4 Product Quality Assessment Specification

5.4.1 Is a Technical Standard Enough?

A manufacturer sends a product to a testing laboratory and receives a test report saying that the product performed successfully.  This is good news, but some important questions remain, such as:

- What future changes to the product would require the re-testing of the product?

- What changes require full re-testing and what changes would require repeating only certain tests?

- If there are no changes, what test(s) must be repeated and how often?

- If structurally similar products are developed, must all of them be submitted for testing?

The Technical Standard does not answer these questions. It only provides the test protocol. Instead, one must look to something called the “Product Quality Assessment Specification” for answers.

5.4.2 What is a Product Quality Assessment Specification”?

A Product Quality Assessment Specification (PQAS) is a document, which describes when testing will be required for a product (for example, a module) or a group of products with “structural similarity”, which is in production for an extended period. The reason for re-testing could be that

- The product is continuously produced for an extended period (e.g. years) of time, or

- The manufacturer has made changes in the materials or components used or in the design of the product.

A “Product Quality Assessment Specification” is basically a manufacturer’s detailed product specification. For a product to be certifiable, it must be described in a detailed product specification.  Standards like the PV Module Qualification Standard, for example, IEC 61215 only specify the test protocol.  They do not describe the manufacturer’s product in detail and, therefore, are not certifiable.  On the other hand, the UL document: UL 1703 is a certifiable standard to which UL certifies PV modules for safety.

Standards organizations usually do not write detailed specifications for manufacturers’ products, because they are all different in one aspect or another. They do, however, write a “Blank Product Quality Assessment Specification” (B-PQAS).  A  B-PQAS is a template to be filled out by the manufacturer for a particular product or series of products.  When completed, it results in a detailed specification, which is the basis for the product’s certification.  It also describes products, which have structural similarity. It also states re-testing requirements, based on industry recommendations.

5.4.3 What is in a Product Quality Assessment Specification?

- Identification of the product

- Qualification approval procedure

- Quality conformance inspection

- Modification of the product

- Requirement(s) for the marking of the product

- Requirement(s) for documentation

Identification of the Product (for example, PV module):

Specifies construction: (for example: glass front, or non-glass; frame material, junction box and other typical construction details

Provides drawings:  an outline drawing with main dimensions that are important

Describes electrical characteristics and configuration: for example: Maximum power (Pmax), voltage at Maximum power (Vmax), etc., and also the current-voltage characteristics.

Qualification Approval:

Defines the overall approval process

Defines requirements for various levels of manufacturing and subcontracting

Provides minimum testing requirements.

Quality Conformance Inspection:

(See Appendix 6, Example of a Product Quality Assessment Specification) (PVRS-2 Table 1 = Test schedule for quality conformance inspection))

Defines requirements for lot by lot acceptance tests

Defines requirements for periodic testing. For example: how often you need to repeat different tests from IEC 61215.

Modifications to the Product, which do and do not Require Re-testing:

(See Appendix 6, Example of a Product Quality Assessment Specification)

Defines which process or product modification require retest

Defines the retest necessary for specific changes to process for the product

Defines which process or product modifications do not require re-testing.

Marking:

(See Appendix 6, Example of a Product Quality Assessment Specification)

Defines what markings shall be on the product

Provides guidance regarding additional information that the manufacturer may want to put on the label

Provides guidance for information that the manufacturer may want to put on the package.

Documentation:

Defines what documentation shall be included with each delivery of the product

May require specific product information to be included in this documentation

Declaration of Conformity declares that the product has been released according to the detail specification under the supervision of the IECQ procedure.

5.4.4 Time Required to Complete the Blank Product Quality Assessment Specification

Manufacturers who completed a Product Quality Assessment Specification  (e.g. for PV modules) have reported that it took them no more than fifteen minutes to complete the B-PQAS.

5.5 Structural Similarity and Product Retest

The concept of Structural Similarity of a product in defining exactly when a product has to be retested is very important for the Manufacturer as well as for the customer. These cost saving concepts are benefits derived from utilizing the IECQ system.

As mentioned before, Technical Standards (for example the IEC 61215) establishes the test protocol. If a product tests successfully, it is expected that the product quality is acceptable, but as mentioned before several questions remain open. For example, if several products are structurally similar, yet some differ in dimensions, than the question is: should every size be tested or is testing of only one size acceptable? The other question concerns whether a product is in production for an extended period of time will need to be retested.  Also, if the manufacturer has made changes in the product, what change is material and requires retesting, and, if retesting is needed, which test should be repeated?

These are important questions for the manufacturer as well as for the customer.  Their answer can:

- Save money for the Manufacturer and

- Eliminate questions as to when or how retesting should be done.

The PQAS addresses these questions. The PQAS reflects the interest of the Manufacturer and also the customer, as the Specifications terms were decided by IEC TC 82 or by PV GAP’s Technical Committee and approved by the Certification Management Committee of the IECQ.

5.5.1 Structural Similarity

The Product Quality Assessment Specification identifies a product (for example, a module) or a group of products with “structural similarity”. If a product’s design, manufacturing method and materials used are the same, but the dimensions of the product, or for example, the power output or power management capabilities of the product are different, then these products could be considered “structurally similar”. In this case, the IECQ system requires the testing of only one type. The Supervising Inspectorate will select the type from the structurally similar products.

A PQAS represents a big savings for the Manufacturer.  In its absence, each customer could require testing of the product the customer is considering buying.

5.5.2 Retest

After successful initial testing, and when a product is in production for an extended period, when would re-testing be required? The reason for re-testing could be that

- the product is continuously produced for an extended period (e.g. years) of time, or

- the manufacturer has made changes in the materials or components used or in the design of the product.

The Product Quality Assessment Specification addresses all of these questions. Again the time when a product should be retested, or which changes will require retesting as well as what tests(s) should be redone has been decided by experts on the basis of the consent of all interested parties. This obviously eliminates questions.  It also informs the Manufacturer what change in material or production could have an effect on its product’s performance.

#### 5.6 Testing Laboratories

As mentioned earlier, a product has to be tested by an accredited or approved testing laboratory to verify that the product passes all tests required in the Standard for that product.  The role of the testing laboratory is to test the PV component and/or system according to an accepted standard. The criteria for an accepted standard and Product Quality Assessment Specification have already been discussed.

PV component and/or system tenders now require that the PV component and/or system should be tested by a testing laboratory that complies with the ISO/IEC 17025 requirements and has been duly accredited by an internationally recognized accreditation organization or approved by IECQ (PV GAP).

The ISO/IEC 17025 is similar in concept to the ISO 9001:2000 requirements.  To establish a Qualified System, the laboratory is required to develop a Quality Manual, which either includes the laboratory's quality system procedures or identifies where they are located.   It is further required to establish a Quality System, writing down what each employee does in each step of the testing process, and making sure that documentation is kept up to date.

5.6.1 The types of accredited or approved Testing Laboratories

The PV GAP (IECQ) approval system for testing laboratories covers two types of laboratories:

- Independent Testing Laboratories, which are defined as organizations in the business of making testing services available to other organizations, and which have the facilities and capability to carry out tests and measurements on PV components or materials in accordance with their specification(s).  Independent Testing Laboratories have to be accredited by a duly recognized accreditation organization. The accepted criteria for an Independent Testing Laboratory accreditation are that the relevant provisions of the ISO/IEC 17025 are met.

- Laboratories that are part of PV manufacturing companies, which have the proper equipment, personnel, traceability, etc. to perform the tests prescribed by the standard(s) and specification(s). The manufacturer has to have  ISO 9001:2000 certification.

Therefore, a PV manufacturer has a choice. The decision will usually be based on cost. The choice gives the manufacturer an opportunity to save money, if the independent laboratories are too costly or not conveniently located, and also to program the testing to suit company convenience.

5.6.2 The Importance of Reciprocity

Reciprocity ensures that a test report for a product tested in a testing laboratory in one country will be accepted in other countries. This saves a large amount of money and time for the PV manufacturer or integrator, by avoiding the need to  re-test a product.

How is global reciprocity of test results achieved?  First, the tests should be performed in an accredited testing laboratory having an ISO/IEC 17025 approval from an internationally recognized accreditation body.  The accreditation certificate should be acceptable to PV GAP or to an SI of the IECQ, or, based on the Manufacturer’s ISO 9001:2000 certificate, approved by a Supervising Inspectorate.

The SI role is to:

- accredit the testing laboratory, or verify that the testing laboratory’s accreditation was done by another internationally accepted accreditation body.

- (If the accreditation was performed by the SI), periodically audit the testing laboratory to make sure that its accreditation has been properly maintained.

The PV GAP role is to:

- have its Accreditation Review Committee ( which has PV experts from several countries ) review the accreditation certificate of a PV Testing Laboratory and, if acceptable, approve the Testing Laboratory. In this case the Laboratory agrees that it will accept test results from other PV GAP-listed or IECQ- accredited testing laboratories. In this case, PV GAP also notifies IECQ of the approval.

In contrast to accreditation bodies, which are national, SIs are connected to each other within the IECQ quality assessment system. Therefore, if one SI accredits a testing laboratory, all the others in every country or region of the world will recognize the tests.  This reciprocity of acceptance of test results under the IECQ system is truly invaluable in a global business, such as solar PV.

A list of Supervising Inspectorates worldwide is provided in Appendix 7. A current list of Testing Laboratories is presented in Appendix 8

5.6.3 Independent Testing Laboratories

### Purpose of Testing Laboratory Quality Systems

Why is it important that a testing laboratory develops, institutes, and maintains quality processes and procedures? A documented quality system, which in the case of Independent Testing Laboratories is the ISO/IEC 17025, that meets recognized standards, does all of the following:

- It demonstrates the laboratory's commitment to quality.

- It provides evidence of the laboratory's internal discipline.

- It indicates consistency and efficiency of work processes.

- It provides a solid foundation for continuous improvement.

- It encourages customer confidence.

- It encourages automatic approval as an unbiased resource.

- It encourages marketplace recognition.

In addition, such a well-defined quality system provides the testing laboratory with the opportunity to identify system inefficiencies, track and correct deficiencies, and continuously improve testing procedures.  All this should significantly improve its success in the competitive market for testing services.

The development of an approved quality system involves a feedback process of continuous assessment, documentation, validation, and revision. The development process generally falls into three broad areas:

- Reviewing, assessing, and documenting the laboratory’s practices and operations

- Implementing the quality system

- Improving the quality system

The key to developing a successful quality process program is to involve all employees in its development. These are the people who do the work on a daily basis; they are the people who are most familiar with what works and what doesn’t; and, they are the people who will be responsible for carrying out any new policies, procedures, and documentation practices.

Unfortunately the ISO/IEC 17025 is similar to the ISO 9001:2000 standard in that it requires experts to interpret it, and is not user friendly. In reviewing the ISO/IEC 17025, PV GAP determined that it could easily and inexpensively be simplified and made relevant for small- or medium-size testing laboratories.  PV GAP subsequently developed the “PV Test Laboratory Quality Manual” (see Bibliography).  This has been reviewed and approved by many organizations, including testing laboratories, auditing organizations and PV manufacturers in both industrialized and developing countries.

Accreditation Process

Accreditation requires recognition as an approved laboratory through a certificate of approval from a duly recognized accreditation organization that itself complies with ISO/IEC Guide 58, Calibration and Testing Laboratory Accreditation System – General Requirements for Operation and Recognition, such as the IECQ or those that are signatory to the APLAC Mutual Recognition Agreement, including NATA, HOKLAS, IANZ, SINGLAS, CNLA, A2LA, and NVLAP. An address list can be requested from the PV GAP Secretariat (Geneva, Switzerland).

Why Must Testing be done by an Accredited Testing Laboratory?

There are two reasons for this requirement:

- One is that organizations that issue tenders for PV components and/or systems plan to invest large amounts of money in PV and are understandably cautious.  They want assurances that they are buying products, which have been tested in a laboratory whose operations comply with existing international standards.  This is also advantageous to manufacturers, because it filters out those manufacturers whose product does not meet specifications, and it helps protect the reputation of the PV Industry

2.   The other reason is the need for global reciprocity of test results that is only provided by the IECQ system.

5.6.4 Manufacturer’s Approved Testing Laboratory

Some PV manufacturers may have good in-house testing capabilities. This is needed for controlling product quality, such as classifying modules according to their output power and for the development of new products. For example, solar cell and module manufacturers usually have a solar cell tester to match cells to be assembled in a module and a sun simulator to test the output of the solar modules. For development work they may have temperature cycling ovens and humidity chambers. Under the IECQ system,  in-house testing laboratories that are part of PV manufacturing companies, and which have the proper equipment, personnel, traceability, etc. that is included in the ISO 9001:2000 certification, are suitable to perform the tests prescribed by the standard(s).

This is an interesting and cost saving aspect of utilizing the IECQ system if the manufacturing company has an ISO 9001:2000 certification, because under the IECQ system, the IECQ’s Supervising Inspectorate (SI) will approve the manufacturer’s in-house testing facility and tests could be made there, under the supervision of the IECQ, while only those tests which the manufacturer is not equipped for have to be sent out to an independent laboratory.

The PV GAP (IECQ) system is of great advantage because an in-house Testing Laboratory  not only saves cost to the manufacturer, but can also accelerate the introduction of new products, and expedite the periodic testing of existing ones as the manufacturer has control over the scheduling of tests.